## Fan Data
Calculation authored and generated by CTC Design, Inc.
Sheet Filename & Title: Fan Laws and Fan HP |  |  | Rev Date: | 2009-06-30
Sheet Rev No: 1 |  |  | Print Date: | 2026-07-29
Information from Fan Manufacturer
Design Airflow | 6000 | CFM
Design Static Pressure | 3 | inches of WC
Fan Speed | 1715 | RPM
Fan Power | 4.69 | BHP
Fan Motor Speed | 1800 | RPM
Drive Type | Belt Driven
Fan Mechanical Effeciency | 75%
Motor Effeciency | 95%
Fan Laws Table
Airflow - CFM | Static Pressure - in | Fan RPM | BHP
1000 | 0.083333 | 285.8333 | 0.021713
1500 | 0.1875 | 428.75 | 0.073281
2000 | 0.33333 | 571.6667 | 0.1737
2500 | 0.52083 | 714.5833 | 0.33927
3000 | 0.75 | 857.5 | 0.58625
3500 | 1.0208 | 1000.4167 | 0.93094
4000 | 1.3333 | 1143.3333 | 1.3896
4500 | 1.6875 | 1286.25 | 1.9786
5000 | 2.0833 | 1429.1667 | 2.7141
5500 | 2.5208 | 1572.0833 | 3.6125
6000 | 3 | 1715 | 4.69
Fan / Motor Sheave Sizing
| Sheave Dia | RPM
Fan | 3 | 2700
Motor | 4.5 | 1800
Motor & Fan Speed vs. VFD Hz.
VFD Hz. | Moter RPM | Fan RPM
5 | 150 | 225
10 | 300 | 450
15 | 450 | 675
20 | 600 | 900
25 | 750 | 1125
30 | 900 | 1350
35 | 1050 | 1575
40 | 1200 | 1800
45 | 1350 | 2025
50 | 1500 | 2250
55 | 1650 | 2475
60 | 1800 | 2700
©CTC Design, Inc. This file and it's content is the exclusive property of CTC Design, Inc. It's intended for CTC Design, Inc. use only and is not to be used by others without written permission from CTC Design, Inc.

## Energy Usage
Calculation authored and generated by CTC Design, Inc.
Sheet Filename & Title: Fan Laws and Fan HP Sizing |  |  | Rev Date: | 2009-06-30
Sheet Rev No: 1 |  |  | Print Date: | 2026-07-29
Fan Energy Usage Table
Airflow - CFM | Fan BHP | Motor HP | Motor kW
1000 | 0.021713 | 0.022856 | 7.7984e-05
1500 | 0.073281 | 0.077138 | 0.0002632
2000 | 0.1737 | 0.18285 | 0.00062387
2500 | 0.33927 | 0.35712 | 0.0012185
3000 | 0.58625 | 0.61711 | 0.0021056
3500 | 0.93094 | 0.97994 | 0.0033436
4000 | 1.3896 | 1.4628 | 0.004991
4500 | 1.9786 | 2.0827 | 0.0071063
5000 | 2.7141 | 2.857 | 0.009748
5500 | 3.6125 | 3.8026 | 0.012975
6000 | 4.69 | 4.9368 | 0.016845
©CTC Design, Inc. This file and it's content is the exclusive property of CTC Design, Inc. It's intended for CTC Design, Inc. use only and is not to be used by others without written permission from CTC Design, Inc.