## Gases LC50 Table
Common Toxic Gases As Defined By The TGO
GAS & FORMULA | CAS No./ UN No. | UBC/CFC Class1 | TGO Class2 | IDLH3 PPM | LC504 PPM | LOC PPM | Max TQ | PEL5 PPM
Ammonia - NH3 | 7664-41-7 UN1005 | Corrosive 6,7 Flammable | III | 300 | 4000 | 30 | 8000 lbs | 50
Arsine - AsH3 | 7784-42-1 UN2188 | Highly Toxic Flammable | I | 3 | 20 | 0.3 | N/A | 0.05
Boron Tribromide - Bbr3 | 10294-33-4 UN2692 | Toxic WR-2 | II | 50 | 380 | 5 | 760 lbs | 1 ©
Boron Trichloride - BC13 | 10294-34-5 UN1741 | Corrosive 6 WR-1 | II | 25 8 | 2541 | 2.5 | 5082 lbs | 5
Boron Trifluoride - BF3 | 7637-07-2 UN1008 | Toxic WR-1 | II | 25 | 806 | 2.5 | 1612 lbs | 1 ©
Bromine - Br2 | 7726-95-6 UN1744 | Highly Toxic Corrosive Oxidizer | I | 3 | 113 | 0.3 | N/A | 0.1
Carbon Monoxide - CO | 630-08-0 UN1016 | Flammable6 | III | 1200 | 3760 | 120 | 7520 lbs | 50
Chlorine - Cl2 | 7782-50-5 UN1017 | Toxic Corrosive Oxidizer | II | 10 | 293 | 1 | 586 lbs | 1 ©
Chlorine Dioxide - ClO2 | 10049-04-4 NA9191 | Toxic UR-3 Oxidizer WR-1 | II | 5 | 250 | 0.5 | 500 lbs | 0.1
Chlorine Trifluoride - C1F3 | 7790-91-2 UN1749 | Toxic Oxidizer WR-3 | II | 20 | 299 | 2 | 598 lbs | 0.1 ©
Diborane - B2H6 | 19278-45-7 UN1911 | Highly Toxic Flammable WR-2 | I | 15 | 80 | 1.5 | N/A | 0.1
Dichlorosilane - SiH2Cl2 (HCl) | 4109-96-0 UN2189 | Toxic Corrosive Flammable | II | 50 | 314 | 5 | 628 lbs | 5 ©
Ethylene Oxide - C2H40 | 75-21-8 UN1040 | Flammable 6 UR-3 | III | 800 | 4350 | 80 | 8700 lbs | 1
Fluorine - F2 | 7782-41-4 UN1045 | Highly Toxic Oxidizer | I | 25 | 185 | 2.5 | N/A | 0.1
Germane - GeH4 | 7782-65-2 UN2192 | UR-3 Toxic Flammable | II | 6 8 | 622 | 0.6 | 1244 lbs | 0.2 9
Hydrogen Bromide - HBr | 10035-10-6 UN1048 | Corrosive 6 | II | 30 | 2860 | 3 | 5720 lbs | 3
Hydrogen Chloride - HCl | 7647-01-0 UN1050 | Corrosive 6 | II | 50 | 2810 | 5 | 5620 lbs | 5 ©
Hydrogen Cyanide - HCN | 74-90-8 UN1051 | Highly Toxic Flammable | I | 50 | 40 | 5 | N/A | 10
Hydrogen Fluoride - HF | 7664-39-3 UN1052 | Toxic | II | 30 | 1300 | 3 | 2600 lbs | 3
Hydrogen Selenide - H2Se | 7783-07-5 UN2202 | Highly Toxic Flammable | I | 1 | 2 | 0.1 | N/A | 0.05
Hydrogen Sulfide - H2S | 7783-06-4 UN1053 | Toxic Flammable | II | 100 | 712 | 10 | 1424 lbs | 20
Methyl Bromide - CH3Br | 74-83-9 UN1062 | Toxic Flammable | II | 250 | 1007 | 25 | 2014 lbs | 20 ©
Methylisocyanate - CH3NCO | 624-83-9 UN2480 | Highly Toxic Flammable WR-2 | I | 3 | 22 | 0.3 | N/A | 0.02
Methyl Mercaptan - CH3SH | 74-93-1 UN1064 | Toxic Flammable | II | 150 | 1350 | 15 | 2700 lbs | 10 ©
Nickel Carbonyl - Ni (CO)4 | 13463-39-3 UN1259 | Highly Toxic UR-3 | I | 2 | 18 | 0.2 | N/A | 0.001
Nitric Oxide - NO | 10102-43-9 UN1660 | Highly Toxic Oxidizer | I | 100 | 115 | 10 | N/A | 25
Nitrogen Dioxide - NO2 | 10102-44-0 UN1067 | Highly Toxic Oxidizer WR-1 | I | 20 | 115 | 2 | N/A | 5 ©
Phosgene - COCl2 | 75-44-5 UN1076 | Highly Toxic WR-1 | I | 2 | 5 | 0.2 | N/A | 0.1
Phosphine - PH3 | 7803-51-2 UN2199 | Highly Toxic Pyrophoric | I | 50 | 20 | 5 | N/A | 0.3
Phosphorus Oxychloride - POCl3 | 10025-87-3 UN1810 | Highly Toxic WR-2 | I | 0.96 8 | 96 | 0.096 | N/A | 0.1 8,9
Phosphorus Pentafluoride - PF5 | 7647-19-0 UN2198 | Toxic Oxidizer WR-1 | II | 2.6 8 | 260 | 0.26 | 520 lbs | 3
Phosphorus Trichloride - PCl3 | 7719-12-2 UN1809 | Toxic UR-2 WR-2 Oxidizer | II | 25 | 208 | 2.5 | 416 lbs | 0.5
Selenium Hexafluoride - SeF6 | 7783-79-1 UN2194 | Highly Toxic | I | 2 | 50 | 0.2 | N/A | 0.05 (as Se)
Silicon Tetrachloride - SiCl4 (HCl) | 10026-04-7 UN1818 | Toxic Corrosive | II | 50 | 750 | 5 | 1500 lbs | 5 ©
Silicon Tetrafluoride - SiF4 (HF) | 7783-61-1 UN1859 | Toxic WR-2 | II | 30 | 450 | 3 | 900 lbs | 0.1
Stibine - SbH3 | 7803-52-3 UN2676 | Highly Toxic Flammable | I | 5 | 20 | 0.5 | N/A | 0.1
Sulfur Dioxide - SO2 | 7446-09-5 UN1079 | Corrosive 6 | II | 100 | 2520 | 10 | 5040 lbs | 5
Sulfuryl Fluoride - SO2F2 | 2699-79-8 UN2191 | Corrosive 6 | III | 200 | 3020 | 20 | 6040 lbs | 5
Tellurium Hexafluoride - TeF6 | 7783-80-4 UN2195 | Highly Toxic | I | 1 | 25 | 0.1 | N/A | 0.02 (as Te)
Titanium Tetrachloride - TiCl4 | 7550-45-0 UN1838 | Highly Toxic Corrosive WR-2 | I | 1.3 | 119 | 0.13 | N/A
Tungsten Hexafluoride - WF6 (HF) | 7783-82-6 UN2196 | Toxic Corrosive WR-2 | II | 30 | 217 | 3 | 434 lbs | 0.1
Notes:
1. Class as defined in CFC: 1.) Health Hazards per Article 2; Highly Toxic = < 200 LC50, Toxic = 200 – 2,000 LC50. 2.) Physical per UFC Standard 79-3.
2. TGO Class Defined As: Class I = <200 LC50, Class II = 200 – 3000 LC 50, Class III = 3001 – 5000 LC 50.
3. IDLH values published in 2005 by the National Institute for Occupational Safety and Health (NIOSH).
4. LC50 data: Lowest reported value, 1 hour adjusted, taken from DOT, CGA, RTECS.
5. PEL values published by OSHA (29 CFR, part 1910.1000, Table Z-1) dated 7/1/95. OSHA values used if available, otherwise TLV from ACGIH or Cal OSHA values
used. © = Ceiling Limit.
6. Moderately toxic as adopted by the cities of San Jose, Santa Clara, and Milpitas: LC50 = 2000 – 5000.
7. When used as a refrigerant, UBC Class does not apply. See TGO consensus guidelines for additional information regarding ammonia refrigeration systems.
8. No. 8 not listed in book
9. Cal OSHA PEL, Title 8, Section 5155, 9/1/95
10. Threshold Limit Values (TLV) from the American Conference of Governmental Industrial Hygienists (1994 – 1995).

## Main Calcs
Calculation authored and generated by CTC Design, Inc.
Sheet Filename & Title: Gas Evaluation of Hazard |  | Rev Date: 4-22-09 | 2009-04-22
Sheet Rev No: 2 |  | Print Date: | 2026-07-29
Binary Mixtures
Gas | Phosphine - PH3
Concentrations | 5%
LC50 | 20
LC50M | 400
Gas Classification * | Toxic
* Depending on the balance gas. The mixture can be classified as flammable.
©CTC Design, Inc. This file and it's content is the exclusive property of CTC Design, Inc. It's intended for CTC Design, Inc. use only and is not to be used by others without written permission from CTC Design, Inc.