## 1st
Inlet Conditions
Flow | 24 | GPM | 3.2083 | ft3/min
Water Temperature | 200 | F
Water Density | 60 | lbm/ft3
Heat Capacity Rate | 38499.84 | btu/min
Outlet Conditions
Flow | 10 | GPM | 1.3368 | ft3/min
Water Temperature | 130 | F
Water Density | 60 | lbm/ft3
Heat Capacity Rate | 10427.04 | btu/min
Tank Conidtions
Tank Volume | 1500 | gal | 200.52 | ft3
Starting Water Temperature - at Time Zero | 60 | F
Water Density | 60 | lbm/ft3 |  |  | C | 2.3333
After 10 Minutes | 200 | minutes |  |  | D | 0.016
Tank Water Temperature | 142.3346 | F
Time - minutes | Tank Water Temperature F
0 | 60
5 | 66.5992
10 | 72.691
15 | 78.3144
20 | 83.5055
25 | 88.2975
30 | 92.7211
35 | 96.8046
40 | 100.5741
45 | 104.0538
50 | 107.2659
55 | 110.2311
60 | 112.9684
65 | 115.4951
70 | 117.8277
75 | 119.9808
80 | 121.9685
85 | 123.8033
90 | 125.497
95 | 127.0606
100 | 128.5039
105 | 129.8362
110 | 131.0661
115 | 132.2015
120 | 133.2496
125 | 134.2171
130 | 135.1102
135 | 135.9346
140 | 136.6956
145 | 137.3982
150 | 138.0467
155 | 138.6454
160 | 139.198
165 | 139.7082
170 | 140.1791
175 | 140.6138
180 | 141.0151
185 | 141.3855
190 | 141.7275
195 | 142.0432
200 | 142.3346
205 | 142.6036
210 | 142.8519
215 | 143.0811
220 | 143.2927
225 | 143.488
230 | 143.6684
235 | 143.8348
240 | 143.9885
245 | 144.1303
250 | 144.2612
255 | 144.3821
260 | 144.4937
265 | 144.5967
270 | 144.6918
275 | 144.7795
280 | 144.8605
285 | 144.9353
290 | 145.0044
295 | 145.0681
300 | 145.1269
305 | 145.1813
310 | 145.2314

## 2nd
Inlet Conditions - Solar
Flow V1 | 24 | GPM | 3.2083 | ft3/min
Water Density | 60 | lbm/ft3
Outlet Conditions - DHW
Flow V2 | 24 | GPM | 3.2083 | ft3/min
Water Temperature - Thi | 170 | F
Water Temperature - Tho | 156 | F
Water Density | 60 | lbm/ft3
Tank Conidtions
Tank Volume | 1500 | gal | 200.52 | ft3
Starting Water Temperature - at Time Zero | 200 | F
Water Density | 60 | lbm/ft3 |  |  | A | 336
After 10 Minutes | 100 | minutes
Tank Water Temperature | 169.3044 | F
Time - minutes | Tank Water Temperature F
0 | 200
5 | 195.2686
10 | 191.2368
15 | 187.8011
20 | 184.8734
25 | 182.3785
30 | 180.2526
35 | 178.441
40 | 176.8972
45 | 175.5817
50 | 174.4607
55 | 173.5054
60 | 172.6914
65 | 171.9978
70 | 171.4067
75 | 170.903
80 | 170.4738
85 | 170.108
90 | 169.7963
95 | 169.5307
100 | 169.3044
105 | 169.1115
110 | 168.9472
115 | 168.8071
120 | 168.6878
125 | 168.5861
130 | 168.4994
135 | 168.4256
140 | 168.3627
145 | 168.309
150 | 168.2634
155 | 168.2244
160 | 168.1912
165 | 168.163
170 | 168.1389
175 | 168.1183
180 | 168.1008
185 | 168.0859
190 | 168.0732
195 | 168.0624
200 | 168.0532
205 | 168.0453
210 | 168.0386
215 | 168.0329
220 | 168.028
225 | 168.0239
230 | 168.0204
235 | 168.0173
240 | 168.0148
245 | 168.0126
250 | 168.0107
255 | 168.0091
260 | 168.0078
265 | 168.0066
270 | 168.0057
275 | 168.0048
280 | 168.0041
285 | 168.0035
290 | 168.003
295 | 168.0025
300 | 168.0022
305 | 168.0018
310 | 168.0016
315 | 168.0013
320 | 168.0011
325 | 168.001
330 | 168.0008
335 | 168.0007
340 | 168.0006
345 | 168.0005
350 | 168.0004
355 | 168.0004
360 | 168.0003
365 | 168.0003
370 | 168.0002
375 | 168.0002
380 | 168.0002
385 | 168.0001
390 | 168.0001
395 | 168.0001
400 | 168.0001
405 | 168.0001
410 | 168.0001
415 | 168.0001
420 | 168
425 | 168
430 | 168
435 | 168
440 | 168
445 | 168
450 | 168
455 | 168
460 | 168
465 | 168
470 | 168
475 | 168
480 | 168
485 | 168
490 | 168
495 | 168
500 | 168
505 | 168
510 | 168
515 | 168
520 | 168
525 | 168
530 | 168

## Discharging Heat
Calculation authored and generated by CTC Design, Inc. |  |  |  |  | Graph Data
Sheet Filename & Title: Hot Water Storage Tank Sizing |  | Rev Date: | 2009-06-30 |  | Time - minutes | Tank Water Temperature F
Sheet Rev No: 1 |  | Print Date: | 2026-07-29 |  | 0 | 200
[5 empty] | 5 | 197.2
[5 empty] | 10 | 194.4
Inlet Conditions - Input (Heat Source) |  |  |  |  | 15 | 191.6
Fluid Flow - V1 | 24 | GPM | 3.2083 | ft3/min | 20 | 188.8
Water Density | 60 | lbm/ft3 |  |  | 25 | 186
Delta T : Inlet - Outlet | 10 |  |  |  | 30 | 183.2
[5 empty] | 35 | 180.4
Outlet Conditions - Output (Heated Fluid) |  |  |  |  | 40 | 177.6
Flow V2 | 18 | GPM | 2.4062 | ft3/min | 45 | 174.8
Detla T DHW | 60 | F |  |  | 50 | 172
Water Density | 60 | lbm/ft3 |  |  | 55 | 169.2
[5 empty] | 60 | 166.4
Tank Conidtions |  |  |  |  | 65 | 163.6
Tank Volume | 1500 | gal | 200.52 | ft3 | 70 | 160.8
Starting Water Temperature - at Time Zero | 200 | F |  |  | 75 | 158
Water Density | 60 | lbm/ft3 |  |  | 80 | 155.2
Duration Time t (At the given Delta T and Flows). | 143 | minutes |  |  | 85 | 152.4
Tank Water Temperature at time t | 119.92 | F |  |  | 90 | 149.6
[5 empty] | 95 | 146.8
[5 empty] | 100 | 144
[5 empty] | 105 | 141.2
[5 empty] | 110 | 138.4
[5 empty] | 115 | 135.6
[5 empty] | 120 | 132.8
[5 empty] | 125 | 130
[5 empty] | 130 | 127.2
[5 empty] | 135 | 124.4
[5 empty] | 140 | 121.6
[5 empty] | 145 | 118.8
[5 empty] | 150 | 116
[5 empty] | 155 | 113.2
[5 empty] | 160 | 110.4
[5 empty] | 165 | 107.6
[5 empty] | 170 | 104.8
[5 empty] | 175 | 102
[5 empty] | 180 | 99.2
[5 empty] | 185 | 96.4
[5 empty] | 190 | 93.6
[5 empty] | 195 | 90.8
[5 empty] | 200 | 88
[5 empty] | 205 | 85.2
[5 empty] | 210 | 82.4
[5 empty] | 215 | 79.6
[5 empty] | 220 | 76.8
[5 empty] | 225 | 74
[5 empty] | 230 | 71.2
[5 empty] | 235 | 68.4
[5 empty] | 240 | 65.6
[5 empty] | 245 | 62.8
[5 empty] | 250 | 60
[5 empty] | 255 | 57.2
[5 empty] | 260 | 54.4
[5 empty] | 265 | 51.6
[5 empty] | 270 | 48.8
[5 empty] | 275 | 46
[5 empty] | 280 | 43.2
[5 empty] | 285 | 40.4
[5 empty] | 290 | 37.6
[5 empty] | 295 | 34.8
[5 empty] | 300 | 32
[5 empty] | 305 | 29.2
[5 empty] | 310 | 26.4
[5 empty] | 315 | 23.6
[5 empty] | 320 | 20.8
[5 empty] | 325 | 18
[5 empty] | 330 | 15.2
[5 empty] | 335 | 12.4
[5 empty] | 340 | 9.6
[5 empty] | 345 | 6.8
[5 empty] | 350 | 4
[5 empty] | 355 | 1.2
[5 empty] | 360 | -1.6
[5 empty] | 365 | -4.4
[5 empty] | 370 | -7.2
[5 empty] | 375 | -10
[5 empty] | 380 | -12.8
[5 empty] | 385 | -15.6
[5 empty] | 390 | -18.4
[5 empty] | 395 | -21.2
[5 empty] | 400 | -24
[5 empty] | 405 | -26.8
[5 empty] | 410 | -29.6
Purpose of this Calculations:
Evaluate storage tank volumetric capacity for a given input & output heat capacity. Storage tank is acting like a capacitor for peak or instantaneous load demand.
Using this Calculations:
Enter the values in the highlighted cells. The user should use discretion in selecting and understanding temperature difference and flows. This spreadsheet only considers the difference in temperature for both input and output heat source. The maximum tank temperature cannot exceed that of the entering heating fluid temperature.
©CTC Design, Inc. This file and it's content is the exclusive property of CTC Design, Inc. It's intended for CTC Design, Inc. use only and is not to be used by others without written permission from CTC Design, Inc.
Explaining this Current Calculations:
This application uses solar panels as the heat source, and city water as the heated fluid. The maximum temperature the solar panels can get is 200F using a 10 degree delta. We can flow 18 GPM of City Water for 143 minutes before the temperature of the tank drops to 120F (Minimum required hot water temperature).