## Pumps Curves
|  |  | Rev Date: | 2009-09-22
|  |  | Print Date: | 2026-07-29
Information from Pump Manufacturer
Design Flow | 900 | GPM
Design Head | 230 | FEET of HEAD
Pump Speed | 1800 | RPM
Pump Power | 74 | BHP
Pump Efficiency | 80%
Pump Laws Table
Flow - GPM | Head Pressure - Ft | Pump RPM | BHP
0 | 0 | 0 | 0
90 | 2.3 | 180 | 0.074
150 | 6.3889 | 300 | 0.34259
225 | 14.375 | 450 | 1.1562
300 | 25.5556 | 600 | 2.7407
450 | 57.5 | 900 | 9.25
442.5 | 55.5993 | 885 | 8.7952
525 | 78.2639 | 1050 | 14.6887
600 | 102.2222 | 1200 | 21.9259
675 | 129.375 | 1350 | 31.2188
750 | 159.7222 | 1500 | 42.8241
885 | 222.3972 | 1770 | 70.3613
900 | 230 | 1800 | 74
Pump Speed vs. VFD Hz.
VFD Hz. | Pump RPM
5 | 150
10 | 300
15 | 450
20 | 600
25 | 750
30 | 900
35 | 1050
40 | 1200
45 | 1350
50 | 1500
55 | 1650
60 | 1800
System CV Calculation
Cv | 2.1
Flow Rate, | 1.5 | GPM
Specific Gravity, SG | 3
Pressure Drop, ∆P | 1.5306 | PSI
| 3.5357 | FT of Head
Calculation authored and generated by CTC Design, Inc.
Sheet Filename & Title: Pump Law Calculation
Sheet Rev No: 2
©CTC Design, Inc. This file and it's content is the exclusive property of CTC Design, Inc. It's intended for CTC Design, Inc. use only and is not to be used by others without written permission from CTC Design, Inc.

## Pump HP & BHP
|  |  | Rev Date: | 2009-09-22
|  |  | Print Date: | 2026-07-29
Pump HP Table
Design Flow | 110 | GPM
Design Static Pressure | 80 | ft
Pump Mechanical Efficiency | 65%
Motor Electrical Efficiency | 75%
Actual Pump HP | 2.2245 | HP
Pump Break HP | 3.4223 | HP
Pump Motor HP | 4.563 | HP
Calculation authored and generated by CTC Design, Inc.
Sheet Filename & Title: Pump Law Calculation
Sheet Rev No: 2
©CTC Design, Inc. This file and it's content is the exclusive property of CTC Design, Inc. It's intended for CTC Design, Inc. use only and is not to be used by others without written permission from CTC Design, Inc.

## Parallel Pump
|  | Rev Date: | 2009-09-22
|  | Print Date: | 2026-07-29
Parallel Pump Table
Static Pressure - Ft | Two Parallel Pumps Flow - GPM
0 | 0
2.3 | 180
6.3889 | 300
14.375 | 450
25.5556 | 600
57.5 | 900
55.5993 | 885
78.2639 | 1050
102.2222 | 1200
129.375 | 1350
159.7222 | 1500
222.3972 | 1770
230 | 1800
Calculation authored and generated by CTC Design, Inc.
Sheet Filename & Title: Pump Law Calculation
Sheet Rev No: 2
©CTC Design, Inc. This file and it's content is the exclusive property of CTC Design, Inc. It's intended for CTC Design, Inc. use only and is not to be used by others without written permission from CTC Design, Inc.